## Overall Data Center Costs
Overall Data Center Costs
Assumptions
| Size of Facility (Critical Load): | 8000000 |  | [Chosen to get ~50k servers -- As PUE improves, critical load goes up without total load changing]
| Cost of power ($/kwh): | 0.07 |  | [Can range betwee just under $0.03 and over $0.15 depending upon region]
| Cost per critical watt in $/W | 9 |  | [Uptime institute says $12.50/W for tier II: http://uptimeinstitute.org/wp_pdf/%28TUI3029A%29CostModelDollarsperkWPlusDollars.pdf]
| Facilities Amortization: | 120 |  | [10 years]
| Watts per Server | 165
| Cost/Server ($) | 1450
| Server Amortization (months) | 36 |  | [3 years]
| Network Amortization (months) | 48 |  | [4 years: most use 5 years today but this is trending down with move to commodity net gear and I think it'll be 3 years soon]
| Annual Cost of Money (%): | 5%
| Average Critical Load Usage (%): | 80% |  | [Average % of provisioned power used]
| Power Usage Effectiveness | 1.45
| Power and Cooling Infrastrucure (%) | 82% |  | [% of infrastructure that is power & cooling -- Christian Belady @ msft]
[Excluding network egress charges, operating system and application stack costs all of which are workload & approach dependent]
Derived from Assumptions
| Size of Facility (Total Load): | 11600000 |  | [MegaWattsCriticalLoad*PUE]
| Number of Servers: | 45977.8788 |  | [(CriticalLoad-NetworkLoad)/WattsPerServer]
| Total Cost of Facility ($): | 72000000 |  | [Critcal Load * CostPerCritical Watt]
Monthly Calculations
| Servers | 1998097.4977 | 56.59% | [=-PMT(CostOfMoney/12, ServerAmortization, ServerCount*ServerCost, 0)]
| Networking Equipment | 294943.0715 | 8.353% | [=-PMT(CostOfMoney/12, NetworkAmortization, NetworkingCost, 0)]
| Power Distribution & Cooling | 626210.802 | 17.74% | [=-PMT(CostOfMoney/12,FacilityAmortization,FacilityCost,0)*PowerAndCoolikngInfrastructurePercentage]
| Power | 474208 | 13.43% | [=MegaWattsCriticalLoad*AveragePowerUsage/1000*PUE*PowerCost*24*365/12]
| Other Infrastructure | 137460.9077 | 3.893% | [=-PMT(CostOfMoney/12,FacilityAmortization,FacilityCost,0)-PowerAndCoolingInfrastructureMonthly]
| Total: | 3530920.2789 | 100%
Fully Burdened cost of Power
| Infrastructure cost of power/Watt/year | 1.1655 | 62.08% | [-PMT(CostOfMoney,+FacilityAmortization/12,+FacilityCost,0)/+WattsCriticalLoad]
| Cost of power/watt/year | 0.7118 | 37.92% | [=+PowerCost/1000*PUE*AveragePowerUsage*24*365.25]
| Fully Burdened Cost of Power: | 1.8773 | 100% | [Fully burdened cost of power per watt per year]

## Networking Gear
Network Cost & Power
Layer | Equipment | Count | Price | Extended Price | Power | Extended Power
Border | Cisco 7609 | 2 | 362000 | 724000 | 5000 | 10000 | [2 border for redundancy]
Core | Cisco 6509E | 2 | 500000 | 1000000 | 5000 | 10000 | [2 core for redundancy]
Aggregation | Juniper Ex8216 | 22 | 750000 | 16500000 | 10000 | 220000 | [2 10Gig to each rack (2x redundancy)]
Access | Cisco 3560-48TD | 1150 | 11995 | 13794250 | 151 | 173650
|  | Net Gear Total: |  | 12807300 |  | 413650
|  | Server Total: |  | 66667924.2424 |  | 7586350
|  | Net Gear as % of Servers: |  | 19.21% |  | 5.767%
Assumptions
| Servers per rack | 40
| Discount Percentage | 60% |  | [Net gear is typically priced silly high and then aggressively discounted to help enterprise equipment buyers feel they are doing their jobs]
| EX8216 "down" ports: | 110 |  | [128 ports total, used 110 down and the rest up to reduce oversubscription]